REVISION OF NAVGUIDE CHAPTER 7

In carrying out this review, it is assumed that the Navguide deals with overview, concepts, broad applications and common practice. It does not deal with narrow applications or common practice, equipment, data or specifics.

# Power Supplies

## Types

A wide range of power systems and energy sources have been used or contemplated for operating lighthouses and floating aids.  Everything from clockwork to radio-active isotopes have been used.  Some of the more common types are listed in Table 7.1.

Table 7.1 Power sources for operating lighted aids to navigation.

| Electric Power Systems | Non-Electric Energy Sources |
| --- | --- |
| - Primary cells | - Acetylene |
| - Mains (utility) electricity supply | - Propane |
| - Diesel and Petrol engine driven generators | - Butane |
| - Photovoltaic Solar modules |  |
| - Wind generators |  |
| - Wave activated generators |  |

### IALA Survey Data on Power Supplies

#### IALA Annual Questionnaire

IALA carry out a questionnaire survey of all IALA Members annually. [insert here what is done with this information and where the information can be accessed]

There is a general trend away from gas, using mains utility electricity where available and photovoltaic solar power where mains is not available.

## Non-Electric

### Acetylene

Acetylene (C2H2) has been used to operate lights on buoys and unattended aids to navigation for many years.  Acetylene can explode if compressed directly, but can be safely contained under low pressure in special cylinders when dissolved in acetone.

The manufacture of acetylene, standards for the cylinders and the filling process are usually controlled by government regulations.

Acetylene has been a convenient and reliable energy source for aids to navigation. However appropriate attention should be given to:

- safe handling of cylinders;

- the broad range of explosive mixtures with air (between 3 and 82% acetylene).

- the purity off the gas, and;

- minimizing leaks in pipe work and fittings;

### Propane

Propane gas (CH3 CH2 CH3) has been used as an alternative fuel to acetylene, particularly in buoys.  Although propane has to be consumed in an incandescent mantle burner to provide a white light, it has several advantages over acetylene:

- it is a by-product in oil refining processes;

- its abundance and low cost;

- propane liquefies at a pressure of 6 atmospheres at 17ºC., and can be transported in quite light and low cost gas bottles;

- propane will maintain a positive pressure down to -40ºC and will not freeze in conditions likely to be encountered at sea;

- placing the bottles in pockets in the buoy or by filling it directly into the body of an buoy, or pressure vessel;

- the comparable containers are the 20 kg propane bottle with gross weight of 48 kg and the 7,000 litre acetylene cylinder, weighing 105 kg;

- furthermore the cost of the propane bottle is only about one-third of that of a acetylene cylinder;

- propane is a particularly safe gas, as only some 6 % of all its possible mixtures with air are explosive against a figure of 80% for acetylene;

- burns cleanly without the risk of sooting that can occur with a poorly adjusted acetylene burner.

Refer also to IALA Practical Notes for the safe handling of gases, October 1993. Refer also to national standards for the safe handling of gas.

## Electric - Non-Renewable Sources

### Primary Cells

Primary cells provide electrical energy by a non-reversible chemical process.  They were used in large numbers up until the 1980s to operate buoys and automatic beacon lights.

#### Zinc-Air Cell

The zinc-air primary cell was a common energy source for operating buoy and beacon applications.  The cell uses a porous carbon block to supply oxygen from the air through an alkaline electrolyte to oxidize a zinc anode.  Individual primary cells have an open circuit voltage of about 1.2 volts and can supply 1000 to 2000 Ah at a maximum rate of about 1 ampere.

#### Others

Add other primary cell types as advised by EEP members.

#### Lithium-Thionyl Chloride Cell

Another type of primary cell in use in buoy applications is the lithium-thionyl chloride cell.  This has a higher energy density and a longer shelf life than the zinc-air cell.

The usage of primary cells has declined sharply since commercial solar power (photovoltaic) modules have become available.  A related issue that hastened the decline of primary cells was the tightening environmental standards in a number of countries that required cells to be recovered from site for disposal in an approved manner.  Disposal compliance costs, and occupational health and safety aspects of the frequent change-out of primary cells have worked in favour of converting to renewable energy sources (eg. solar, wind and wave generators).

#### Sea-Water Cells

The sea-water cell developed for buoy applications in Norway is a primary cell that uses a magnesium anode and a largely inert copper cathode.  The sea water acts both as an electrolyte and the provider of dissolved oxygen for the cathode.

A single cell is installed as part of the buoy tail-tube.  The motion of the buoy has a beneficial effect in agitating the water to provide an oxygen-rich flow through the cell and carry away the reaction products.

Copper was selected for the cathode material because of its inherent antifouling properties.  A magnesium anode was considered environmentally acceptable because it is a naturally occurring element of sea water.  The cell produces a voltage of 0.8 to 1 volt under load.  Components of the cells under evaluated have been sized to provide around 35,000 watt hours of energy.

Since it is impractical to use more than one cell due to the current leakage that would occur, a dc-dc converter is used to raise the voltage to the level required by the load.

### Internal Combustion Engine/Generators

#### Diesel Generators

Diesel engine driven generators are often used as the primary source of electrical power where the location of a lighthouse is too remote to be supplied from a mains electricity grid.  Diesel generators are also used to provide emergency or backup power.

The generator capacity to support the operational and domestic loads of a lighthouse would be in the range of 10 to 30 kW.  Diesel generators of this size could be expected to consume around 0.4 litres/kWh.

The requirement for diesel generators in lighthouses is decreasing as a result of:

- lighthouse automation (destaffing), and because;

- new beacon and lamp technology that enables a light with a nominal range 18 to 20 nautical mile to be operated from a renewable energy source.

#### Petrol-engine Generators

Petrol-engine generators are a useful source of power for maintenance work, but are less common in permanent installations due to:

- fuel and fuel storage safety issues;

- maintenance requirements on the spark-ignition system, and;

- the petrol engine generally being regarded as less durable than a diesel.

### Other

Some of the less common power generating equipment considered for aids to navigation applications are mentioned below.

#### Thermo-electric generator

- This is a solid-state generator in which a heat source, commonly from a propane burner, is directed onto a thermopile (ie. an array of thermocouple type elements).  Since each thermocouple only produces a voltage of around 0.5 volts, a number are connected in series;

- This type of generator has a low thermal efficiency (around 5%) and is rarely used.

#### Stirling engine driven generator

- The Stirling engine is an external combustion engine that can be operated on gas or diesel fuel.  Packaged generator sets are available that could operate a lighthouse.  Typical generators produce 1kW electrical output and 5kW of heat.  The heat output could be a useful by-product for building conditioning in a lighthouse.

#### Fuel cell

- This is a solid-state device that uses a catalytic process to oxidise fuel to generate an electrical current. A common fuel is hydrogen, or hydrogen rich fuels.  It can be thought of as a continuously fed battery.

- The commercial fuel cell is still an emerging technology and at this stage is an expensive power source.  Aids to navigation applications are likely to be limited to situations where solar energy (photovoltaic) is impractical due to limited insolation or icing conditions.

## Electric - Renewable Energy Sources

### Solar Power (Photovoltaic cell)

#### Aids to Navigation Applications

Solar power is an ideal power source for many aids to navigation applications.  It offers:

- a power source with no moving parts;

- no maintenance requirements other than being cleaned;

- negligible deterioration in power output over its life;

- low life-cycle costs;

When used to power a light, the battery recharging process is separated from the operation of the light so that the recharge voltage can be optimised without detriment to lamp life.

The potential difficulties associated with solar power are:

- finding ways to minimise bird fouling;

  - mounting solar modules vertically is probably the best long-term solution for buoys;

- sizing arrays to operate at high latitudes;

- protecting solar modules from;

  - wave damage on buoys;

  - vandalism and theft

  - lightning.

Aids to navigation exposed to icing conditions are perhaps the only applications unsuited to the use of solar modules.

See IALA specification for solar photovoltaic systems. (1988), See IALA practical note on the application of solar power systems for aids to navigation, September 1993, See IALA Guidelines for renewable energy sources for marine aids to navigation – solar photovoltaic systems, October 1997, IALA is studying the feasibility of developing an IALA Computer program for sizing solar power supplies.

#### Types

There are three common technologies employed in the manufacture of silicon based, solar modules and are listed in Table 7.3 :

Table 7.3 Silicon solar cell technology.

| Type (Technology) | Comments |
| --- | --- |
| Monocrystaline cells | Are made from a thin slice cut from a single large crystal of silicon, usually produced as a circular section rod. Generally have the highest efficiency of the three technologies, If circular wafers of silicon are used the module fill factor is significantly less than with polycrystalline cells. It is now usual for the cells to be trimmed to approximate a square. |
| Polycrystaline cells | Are made from a thin slice cut from a large cast billet of silicon comprising many crystals Are slightly less efficient than the mono crystalline cell but they can be shaped to completely fill the module. |
| Amorphous module | Are made by depositing thin films of silicon directly onto a glass or stainless steel substrate a thin slice cut from a single large crystal of silicon. The cell has a lower efficiency than either of other technologies but can be multi-layered for enhanced performance. Problems have been found with lifetime of these cells. |

In addition to the silicon cell technologies, there are two optional module configurations based on the numbers of series connected cells.  The standard module normally has 36 cells in series to give an open circuit voltage of around 20 volts.  For 12 volt battery charging applications, a voltage (charge) regulator is considered essential.

A self-regulating solar module was promoted as a means of eliminating the voltage regulator that had frequently been found to be the least reliable component in a solar power supply.  The self-regulating module typically has 32 cells in series to give an open circuit voltage of around 18 volts (and a maximum on load voltage of around 15 volts). In a self-regulating solar module, the charging rate is determined by the interaction between the electrical characteristics of the battery and solar module.

- Both concepts can be made to work well.

#### Module or Array Orientation

In the northern hemisphere, solar modules are normally installed facing south and inclined at an angle to the horizontal that is related to the latitude of the site.

The inclination angle for solar modules is often optimised for the particular site as part of the sizing calculations.  Confirm that the table is shown in the solar specification.

One of the main problems experienced with solar powered aids to navigation has been bird fouling.  Numerous ingenious solutions have been trialed, generally with mixed results.  Generally solar modules mounted at an angle or vertically benefit from self washing from rain.

The cost of additional solar modules needed for a vertical installation may be largely off-set by the savings that result from simplifying the mounting arrangements or framework.

### Wind Energy

#### Aids to Navigation Applications

Wind generators (or wind turbines) have been used by a number of IALA Members to power aids to navigation.  The most popular type were horizontal axis machines with a two bladed (propeller type) turbine. The maintenance requirements arising from the moving parts design of wind generators and susceptibility to storm damage has limited the use of wind generators.

IALA published a specification for medium sized wind generator systems in 1988.

#### Installations

Wind generator installations at aids to navigation sites pose a number of problems:

- wind generators tend to require a lot of maintenance if operated in turbulent air flows:

- if the wind generator is installed on a separate mast some distance from the lighthouse, consideration has to be given to cable voltage drop:

- the size of wind generator likely to be considered for operating aids to navigation is at considerable risk of damage if there are populations of birds at the site.

#### Wind Generator Types

A comparison of the typical performance of different types of wind generators is shown in Fig 7.2.

Fig 7.2

### Wave Energy

#### Wave Activated Generator

The wave activated generator (WAG) was developed in Japan and has been successfully used to power lighted buoys.  The interaction between the buoy and wave motions acts as a simple air pump that is used to drive an air turbine and generator.  The WAG is mounted on an extension of a hollow tail tube that passes through the buoy hull.  With wave heights of 0.5 metres, the power output is almost 100 watts.  WAG’s have limited life and current systems suffer from excessive wear.

Site conditions will determine the rate at which the tail tube of the buoy accumulates weed and other forms of fouling, and these aspects need to be taken into consideration when developing the maintenance regime for the WAG. WAG’s can also be very susceptible to storm damage.

## rechargable Batteries

### IALABATT 1 to 4

In recognition of the importance of battery technology in the operation of the modern aids to navigation, IALA has held four workshops on battery related topics for the benefit of members and manufacturers.  The first was held in Bulgaria in 1987 and subsequently in France in 1993 &1997, and combined with IALALITE in Germany, in 2001.  Reports on the proceedings are available as IALA Publications.

### Principal types

There are two main types of storage battery technologies applied to aids to navigation:

- lead acid;

- nickel cadmium.

- Are there other types ???

The lead acid type is generally preferred because of its lower cost and higher energy exchange efficiency (95% vs. 80%) than the nickel cadmium battery.  However, the nickel cadmium battery can operate in lower temperatures and for a greater number of deep discharge cycles.

### Lead Acid

The basic form of this battery uses a lead dioxide positive plate and a lead immersed in an electrolyte of dilute sulphuric acid.  These were originally wet or flooded cells.  However in recent years various forms of “sealed” cell batteries have become available and are quite common in aids to navigation applications.

#### Flooded Lead-Acid Cells

There are three main types of flooded lead acid cell in general use:

- Plante Cells:- that have a pure lead positive plate with a large surface area, in which active material is formed from the lead of the plate itself.

- Tubular Plate Cells:-that use a tubular plate for the positive electrode.  The active material is contained in permeable insulating tubes through which the electrolyte can diffuse.

- Pasted Plate Cells:- in which the positive electrode is a pasted plate consisting of active material formed from oxides or salts of lead pressed into a lead alloy plate of grid form.

#### Valve Regulated Lead-Acid Cell (VRLA)

The VRLA comes in two types:

- AGM:- (absorbed glass-mat) that use a micro glass separator system to absorb the electrolyte.

- Gel Batteries:- that use a gelified electrolyte and polymeric separators to prevent short circuits between the positive and negative plates.

Both types have no “free electrolyte” and the batteries theoretically can be used in any position without acid leakage.  It is recommended that feature be confirmed before system designs are finalised.

The batteries use an oxygen recombination process so that normally there is no gassing. However, a safety valve is provided to release any excess pressure.

Operational characteristics of the battery include:

- a 5-10 year life on float-charge applications;

- tolerance to deep discharge cycles (ie. 80%);

- gradual loss of capacity in cycling applications compared with a flooded cell.

### Nickel Alkaline Battery

These batteries use compounds of nickel and, generally, cadmium with a solution of potassium hydroxide as the electrolyte.

Nickel-cadmium cells use perforated steel plates that hold the active material, mainly a nickel hydroxide in the positive plate and a cadmium compound in the negative plate.  The construction is generally referred to as a "pocket plate” cell.

A range of valve regulated nickel-cadmium batteries that use a recombination process now complement the traditional flooded cell design.  Under normal float charging conditions any gas produced is recombined within the battery and water loss is negligible.  However if the battery is overcharged it will vent but water can be added if necessary.

### Technical Considerations

#### Flooded cell or “Sealed”

The traditional lead acid and nickel cadmium flooded cell technologies have provided good service in many lighthouses and other fixed aids to navigation.  Large capacity flooded cell batteries (or “wet cells”) have a considerable cost advantage for large installations.  However sealed batteries offers some important advantages that include:

- suitability for both floating and fixed aids;

  - facilitates standardisation;

  - reduces on-site maintenance (work, time and cost);

- safer to transport and handle;

  - reduced risk of occupational injuries from electrolyte spills;

  - encourages recovery for appropriate disposal;

  - a less hazardous cargo for helicopters and small boats.

#### Technical Comparison

Table 7.4 shows some of the technical differences between the lead-acid and nickel cadmium batteries.

Table 7.4 A comparison of the performance characteristics of lead-acid and nickel cadmium batteries.

| Type (Technology) | Operating Temperature | Self-Discharge Rate Per Month | Cycle Life to 80% DoD at 40ºC | Ah Charge Efficiency from 20% Discharged to 100% at 25ºC | Relative Cost (1990) |
| --- | --- | --- | --- | --- | --- |
| Tubular-plate flooded | -15 to 55 | 2 | 1800 | 83 | 1 |
| Flat plate flooded | -15 to 55 | 2 | 1200 | 80 | 1 |
| Tubular-plate VRLA | -30 to 50 | 3 | 1000 | >90 | 1.6 |
| Flat plate VRLA | 5 to 50 | 1 | 500 | >90 | 2 |
| Pocket plate VR | -40 to 50 | 2 | 2000 | 71 | 3.9 |
| Pocket plate flooded | -40 to 50 | 4 | 2500 | 71 | 3.9 |

### Battery Disposal

A number of countries now have standards and regulations relating to the safe and environmentally acceptable methods of disposing or recycling of batteries.  The topic was also addressed during IALABATT 3

See also IALA Guidelines on Maintenance, Operation and Safe Handling of Batteries.

## Electrical Loads and Lightning Protection

### Electrical Loads

The requirement for IALA to prepare standard methodology for calculating and defining the load profile of electric aids to navigation arose at IALABATT 2 and reconfirmed at IALABATT 3.  IALA has produced a comprehensive Guideline covering the loads for:

- lights;

- racons

- electric sound signals

- fog detectors

- monitoring and telemetry systems

- charge controllers

- signal control equipment

Refer to the IALA Guidelines on a standard method for calculating and defining the load profile of electric aids to navigation, December 1999.

### Lightning Protection

To assist those engaged in the design of aids to navigation, IALA has produced Guidelines to describe practical methods for the design, installation, inspection and testing of lightning protection systems.  The information covers lightning protection for aids to navigation structures, equipment and systems.

Refer to the IALA Guidelines for the protection of lighthouses and aids to navigation against damage from lightning.

The chemistry of the sea-water cell and the prototype light buoys using this cell have been described in papers for the 1990 IALA Conference and IALABATT 2 and 3.

Refer to IALABatt 3  “Fuel cells for aids to navigation”.

Table adapted from IALABATT 2 Overview of PV Battery Charging, Hyperion Energy Systems Ltd, Ireland.